## Cover sheet
Cover sheet | Affinity Water
Purpose | This spreadsheet provides key market information for a water company's water resource zone (WRZ). Separate spreadsheets are provided for each WRZ and the information provided is in line with guidelines published by Ofwat on its website. Where available companies are required to provide responses to all data.
Company name | Affinity Water | Insert image of WRZ boundary (same as GIS shapefile)
WRZ name | Pinn
WRMP the data relates to | fWRMP19
Date the spreadsheet was first published | 7th February 2018
Date of last update (see change log for details) | 28.05.2020
Contact details for anyone wanting to discuss commercial opportunities arising from this information | wrmpcomms@affinitywater.co.uk
Geographical Information System (GIS) shapefile of water resources zone boundary file reference (hyperlink) | If required, please request using above email address.
Brief description of data assurance | Tables 2 to 8 were populated using previously audited WRP Tables. Table 1 uses data from verified internal sources. A two-tier review process with additional verification was then applied to check and quality assure.
Our data requirements are structured around geographic data and eight data tables:
Key: Input cell colour
Table 1: Key market information - A high level summary of information about the area and location of the WRZ, the current water resources, a summary of the supply-demand balance problem (if any), a summary of treatment capacities and constraints, and any other considerations that may impact solutions. Note this table is predominately based on data outside or supporting the WRMP process. In contrast the other seven tables link to existing WRMP19 data tables.
Table 2: Baseline supply forecast - A more detailed overview of the baseline supply situation for the WRZ. This gives a breakdown of supply availability forecasts for the company’s planning period. Supplies include water available from reservoirs, rivers or groundwater (boreholes) whilst also accounting for treatment and transport constraints. These baseline forecasts assume no new investments or interventions by the company.
Table 3: Baseline demand forecast - A more detailed overview of the baseline demand situation for the WRZ. This gives a breakdown of demand forecasts for the company’s planning period. Demand includes the amount of water required to supply customers whilst also meeting other demands (e.g. leakage) as part of this activity. These baseline forecasts assume no new investments or interventions by the company.
Table 4: Baseline supply demand balance - A more detailed overview of the baseline supply-demand balance for the WRZ. This takes the demand forecasts from the supply forecasts to calculate whether a zone is in a surplus or a deficit over the planning period. This baseline forecast assumes no new investments or interventions by the company.
Table 5: Final plan supply forecast - A detailed overview of the final plan supply situation for the WRZ. This gives a breakdown of the final plan supply availability forecasts for the company’s planning period. These final forecasts are based on the company’s preferred options (new investments and interventions) being completed.
Table 6: Final plan demand forecast - A detailed overview of the final plan demand situation for the WRZ. This gives a breakdown of the final plan demand forecasts for the company’s planning period. These final forecasts are based on the company’s preferred options (new investments and interventions) being completed.
Table 7: Final plan supply demand balance - A detailed overview of the final plan supply-demand balance for the WRZ. This takes the final plan demand forecasts from the final plan supply forecasts to calculate whether a zone will be in a surplus or a deficit over the planning period. This final plan forecast is based on the company’s preferred options (new investments and interventions) being completed.
Table 8: Final plan option costs - A cost breakdown of the feasible options included in the company’s WRMP to solve a planning period deficit. An option is feasible if it has passed through the companies screening process and is technically workable. These may be to increase available supply or reduce forecast demand (both would benefit the supply-demand balance). The costs are broken down into components such as capital costs (Capex) and operating costs (Opex) provided as a discounted total for the life of the solution (Net Present Value). Also, included is the incremental cost of providing these solutions reported as a cost (pence) per additional unit of water delivered or saved (m³).

## Change log
Change log |  | Affinity Water
Date of change (DD/MM/YYYY) | Table Reference | Data Requirement Reference | Description of value(s) changed | Change reason
05.03.2018 | Version 3 |  | All cells populated. To be published online.
28.05.2020 | Version 4 |  | Cells updated to reflect revised fWRMP19. Final version checked against fWRMP19 WRP Tables | Cells updated to reflect published fWRMP19.

## Table 1
Table 1 : Key market information
Company name |  |  | Affinity Water
WRZ name |  |  | Pinn
Data Requirement | WRMP19 reference | Units | Description | Company Reponse
Water Resource Zone location | N/A | Region / Counties | The water resource zone (WRZ) is the largest area of a company’s supply system where all customers have the same water supply risk. This is the level that water resources are managed and new investment planned by the companies through the water resource management plan (WRMP) process. The information should be presented as both a text description and as a boundary file that can be imported to a Geographical Information System (GIS) (such as an ESRI Shapefile). | WRZ4. See map in Cover Sheet (Column E). | See cover sheet.
Total number of sources | N/A | Number | A numeric count of the number of raw water sources for the WRZ location. The total for all of the WRZs should be the same as set out in the company’s Annual Performance Review (APR). | 4
Own source allocation: groundwater (including aquifer recharge) | N/A | % of demand met (distribution input) | The ratio of demand met (distribution input – flow entering the distribution network) from groundwater sources to total demand met. Aquifer recharge is the artificial replenishment of groundwater. The total across all zones should be the same as reported in the company APR. | 15.48
Own source allocation: reservoir (pumped and impounding) | N/A | % of demand met (distribution input) | The ratio of demand met (distribution input – flow entering the distribution network to meet demand) from reservoir sources to total demand. The total across all zones should be the same as reported in the company APR. | 0
Own source allocation: direct river abstraction | N/A | % of demand met (distribution input) | The ratio of demand met (distribution input – flow entering the distribution network to meet demand) from direct river sources to total demand. The total across all zones should be the same as reported in the company APR. | 84.45
External source allocation (trading – imports) | N/A | % of demand met (distribution input) | The ratio of demand met (distribution input – flow entering the distribution network to meet demand) from external sources (third party imports) to total demand. | 0.07
Critical planning period | N/A | % of demand met (distribution input) | The critical planning period as reported in the water resources management plan. This is the period that best highlights the pinch points in the company’s system. The duration of critical period for the supply system should be reported e.g. Dry Year Annual Average (DYAA), or Dry Year Critical Period (DYCP) (defined as week, month, etc.). Where different problems are posed by alternative critical periods – the data tables should be presented for all scenarios. | DYCP (Week)
Level of service (Temporary Use Ban) | N/A | 1 in X | The level of service is the commitment made by each company to all of its customers, based on an understanding of their priorities (e.g. frequency that hosepipe bans are acceptable), following engagement with them. There will be a variation of level of service provided by each company generally based on customer priorities, geography and inherent water resources. The Temporary Use Ban allows for restrictions on a customer’s water usage for activities such as using hosepipes to water gardens. The level of service (average planned frequency) for Temporary Use Ban is a commitment made by companies based on an understanding of customers’ priorities. | 1 in 10 years
Level of service – (Drought order for non-essential use ban) | N/A | 1 in X | The level of service (average planned frequency) for Drought order for non-essential use. This restricts customers’ water usage further for activities such as cleaning the outside of buildings. An ordinary drought order can be applied for by either water companies or the Environment Agency/Natural Resources Wales in a drought situation. | 1 in 40 years
Level of service – Emergency drought order (reducing demand): rota cuts and standpipes | N/A | 1 in X | The level of service (average planned frequency) for an emergency drought order (restricting demand): rota cuts and standpipes as agreed with the company’s customers. Emergency drought orders go further than ordinary drought orders as they enable a water company to have complete discretion on the uses of water that may be prohibited or limited, and to authorise supply by stand-pipes or water tanks. | We do not view standpipes as acceptable, standpipes would only be deployed in the event of a civil emergency. In the event that the drought was to reach this level of severity then our Emergency Plan would be implemented in particular areas of signficant water stress.
Summary key cause of supply constraint | N/A | Hydrological / Licence / Capacity | The limiting factor for the WRZs supply forecast. Supply can be constrained by the amount available from the environment (hydrological / source yield constraint), the amount available via an abstraction licence (licence constraint), or the amount available as defined by a constraining asset such as a pump or pipe capacity (asset constraint). | All sources are licenced constrained.
Drought plan option benefits | Table 10 – Drought Plan links | Ml/d | The benefit that the company believes drought plan actions can contribute to the supply demand balance. These actions are normally short term operational actions that can have a small supply benefit. They are implemented based on hydrological triggers (river flows/reservoir levels) in the company drought plans. | 0Ml/d
Year of first zonal deficit (if any) | N/A | Year | Defines the timing of the problem. This is based on the baseline supply-demand balance (supply forecast minus demand forecast including target headroom allowance – see below). The first year that there is a net water deficit according to the company’s baseline plan | 2020/21
Zone deficit summary | N/A | High (>10%) / Medium (5-10%) / Low (<5%) | Defines the scale of the problem. Relative measure of the zonal deficit from the baseline supply-demand forecast (supply forecast minus demand forecast allowing for target headroom). The maximum forecast deficit (if any) for the first 25 years of the company’s planning period as a percentage of demand (distribution input). | 23.24% (High at 77.51Ml/d in deficit, 333.52Ml/d DI in 2044/45)
Other planning considerations and constraints | N/A | Free text | Any further considerations or constraints that may influence the choice of solutions for the WRZ. These could be source, treatment or transport considerations. Water quality constraints in terms of treatment processes (where this is beyond normal) e.g. proportion of treatment capacity that cannot treat river water, or that cannot treat certain water quality parameters. Treatment capacity/infrastructure capacity constraints – where additional source yield may need to be supplemented with additional investment. | n/a
Treatment works details | N/A | Free text | Anonymised list of treatment works supplying this WRZ which have maximum design capacities greater than 10Ml/d, this should focus on the larger treatment works within the zone where spare capacity will be relatively larger and more proportionate. This list will detail the maximum treatment design capacity, spare capacity (average for critical planning scenario – e.g. year or week), treatment works type (e.g. surface water or groundwater), treatment type and constraints. These should be provided for year 1 of the planning period and then updated to represent the current position. e.g. Works 1 – 50Ml/d – 5Ml/d – surface water – Full treatment Works 2 – 15Ml/d – 2Ml/d – groundwater – Ultraviolet treatment | Works 1 - 20Ml/d - 0Ml/d - Groundwater - W3 Works 2 - 20.46Ml/d - 0Ml/d - Groundwater - W4 Works 3 - 227.3Ml/d - 2.3Ml/d - Surface Water - W5
| Works Category | Treatment Description | Unit Processes Available
| SD1 | Disinfection only at this site. | ~Marginal Chlorination ~Pre-aeration
| W1 | Disinfection with basic physical treatment | ~Slow sand filters ~Rapid gravity filters ~Pressure filters
| W2 | Single stage complex physical/chemical treatment | ~Coagulation ~Flocculation ~Biofiltration ~Softening ~pH correction ~Super chlorination
| W3 | Multiple stage complex physical/chemical treatment (excluding W5, W6 or W7)
| W4 | Single stage complex physical/chemical treatment (Higher operating cost than W3/W4) | ~Ozone ~UV Treatment ~Activated Carbon ~Nitrate/Arsenic/Pesticide Removal ~Membrane Filtration
| W5 | Multiple stage complex physical/chemical treatment (High cost)
| W6 | Works with one or multiple extremely high cost processes. | ~Reverse Osmosis ~Reuse

## Table 2
Table 2 : Baseline supply forecast
Company name |  |  | Affinity Water
WRZ name |  |  | Pinn
|  |  |  | Minimum Planning Period - 25 years | [24 empty] | Optional Planning Period
Data Requirement | WRMP19 reference | Units | Description | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54 | 2054-55 | 2055-56 | 2056-57 | 2057-58 | 2058-59 | 2059-60 | 2060-61 | 2061-62 | 2062-63 | 2063-64 | 2064-65 | 2065-66 | 2066-67 | 2067-68 | 2068-69 | 2069-70 | 2070-71 | 2071-72 | 2072-73 | 2073-74 | 2074-75 | 2075-76 | 2076-77 | 2077-78 | 2078-79 | 2079-80 | 2080-81 | 2081-82 | 2082-83 | 2083-84 | 2084-85 | 2085-86 | 2086-87 | 2087-88 | 2088-89 | 2089-90 | 2090-91 | 2091-92 | 2092-93 | 2093-94 | 2094-95 | 2095-96 | 2096-97 | 2097-98 | 2098-99 | 2099-100 | 2100-101
Deployable output forecast (supply) | Table 2: Baseline supply Row: 7BL | Ml/d | This information is for the baseline forecast before any of the adjustments due to changes or losses. This gives a measure of water supply available at treatment works outlet based on planned level of service and critical period in the current situation. Deployable output is a building block in determining water supplies available for use and is defined as the output for specified conditions for a water resources system as constrained by; hydrological (source) yield; licensed quantities; abstraction assets; raw water transfer assets; treatment; water quality; and levels of service. | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039 | 263.039
Change in deployable output (supply) forecast due to climate change | Table 2: Baseline supply Row: 8.1BL | Ml/d | The forecast reductions in the baseline deployable output (supplies) over the planning period caused by climate change. Climate change is likely to impact the frequency and severity of more extreme events which impact the amount available for supply. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Deployable output (supply) forecast reductions to restore sustainable abstraction (abstraction licence reductions) | Table 2: Baseline supply Row: 8.2BL | Ml/d | Some catchments are reaching the limit of sustainable abstraction or even are over abstracted. Abstraction reductions (to lower levels than current under licence) may be required to protect conservation sites or to deliver Water Framework Directive (WFD) objectives. These are forecast as reductions in deployable output (supply) from the baseline forecast. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total other changes to deployable output (supply) forecast (e.g. nitrates) | Table 2: Baseline supply Row: 8.3BL | Ml/d | Reductions in deployable output (supply) forecast as a result of other causes. These can include operational decline or loss of raw water source due to long term pollution, or other water quality issues. | 7.207 | 7.2227 | 7.1256 | 6.8951 | 6.6772 | 6.541 | 6.4994 | 6.5138 | 6.5699 | 6.626 | 6.6817 | 6.738 | 6.794 | 6.8501 | 6.9071 | 6.9635 | 7.0206 | 7.0771 | 7.1347 | 7.1925 | 7.2497 | 7.3153 | 7.3805 | 7.4469 | 7.5132 | 7.5548 | 7.6151 | 7.6756 | 7.7363 | 7.797 | 7.8579 | 7.9187 | 7.9793 | 8.0397 | 8.0996 | 8.1591 | 8.2178 | 8.2768 | 8.3362 | 8.3967 | 8.4586 | 8.5185 | 8.5783 | 8.6381 | 8.6978 | 8.7575 | 8.8173 | 8.8771 | 8.9371 | 8.9971 | 9.0573 | 9.1174 | 9.1775 | 9.2374 | 9.2971 | 9.3568 | 9.4168 | 9.4768 | 9.5368 | 9.5968
Raw water losses, treatment works losses and operational use | Table 2: Baseline supply Row: 9BL | Ml/d | The water losses as part of the raw water distribution and water treatment activities. Raw water distribution losses can be from pipes, mains, aqueducts, open channels, break pressure tanks and small reservoirs. Raw water operational use can include loss from regular washing-out of mains. Treatment works losses are made up of both continuous and intermittent over-flows. Treatment works operational use includes water lost as a result of the treatment process, i.e. net loss that excludes water returned to source water This may be calculated as the difference between total water abstracted and total distribution input (flow leaving treatment works to meet demand), or may consist of measured values of each component. | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364
Outage allowance | Table 2: Baseline supply Row: 10BL | Ml/d | Supplies from treatment works and abstraction assets are not always available, this is known as outage. They will be temporarily unavailable due to both planned and unplanned maintenance. Generally outage only considers reductions in output for periods less than 3 months, outage for longer than 3 months in most cases will be reflected as a reduction in base deployable output. The outage allowance forecast is based on asset outages within the zone that may result in a reduction in the amount of water available from treatment works. This forecast represents the baseline position before any new investment or interventions. | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311

## Table 3
Table 3 : Baseline demand forecast
Company name |  |  | Affinity Water
WRZ name |  |  | Pinn
|  |  |  | Minimum Planning Period - 25 years | [24 empty] | Optional Planning Period
Data Requirement | WRMP19 reference | Units | Description | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54 | 2054-55 | 2055-56 | 2056-57 | 2057-58 | 2058-59 | 2059-60 | 2060-61 | 2061-62 | 2062-63 | 2063-64 | 2064-65 | 2065-66 | 2066-67 | 2067-68 | 2068-69 | 2069-70 | 2070-71 | 2071-72 | 2072-73 | 2073-74 | 2074-75 | 2075-76 | 2076-77 | 2077-78 | 2078-79 | 2079-80 | 2080-81 | 2081-82 | 2082-83 | 2083-84 | 2084-85 | 2085-86 | 2086-87 | 2087-88 | 2088-89 | 2089-90 | 2090-91 | 2091-92 | 2092-93 | 2093-94 | 2094-95 | 2095-96 | 2096-97 | 2097-98 | 2098-99 | 2099-100 | 2100-101
Measured (metered) non household – consumption | Table 3: Baseline demand Row: 23BL | Ml/d | Non-households are those properties that are not used as dwellings. Measured refers to properties that are metered which affects how much water is used by customers and provides a better forecast of overall water usage (when compared to unmeasured). This provides a forecast of the total water usage (consumption) of the properties that fall into this category. This figure applies to billed measured non-household properties and excludes underground supply pipe leakage. This forecast represents the baseline position before any new investment or interventions. | 32.0771 | 32.2784 | 32.4807 | 32.6848 | 32.8901 | 33.1024 | 31.8303 | 31.8505 | 31.8748 | 31.9022 | 31.9326 | 31.9673 | 32.0071 | 32.051 | 32.0988 | 32.1508 | 32.207 | 32.2674 | 32.3323 | 32.4019 | 32.4759 | 32.5549 | 32.6387 | 32.7274 | 32.8211 | 32.9197 | 32.9167 | 32.9951 | 33.0739 | 33.1525 | 33.2307 | 33.308 | 33.3842 | 33.4591 | 33.5325 | 33.6046 | 33.6756 | 33.7461 | 33.8169 | 33.8892 | 33.9649 | 34.0462 | 34.1189 | 34.1913 | 34.2637 | 34.3363 | 34.409 | 34.4821 | 34.5556 | 34.6294 | 34.7035 | 34.7777 | 34.8517 | 34.9254 | 34.9986 | 35.0714 | 35.1442 | 35.2179 | 35.2917 | 35.3654
Unmeasured (unmetered) non household – consumption | Table 3: Baseline demand Row: 24BL | Ml/d | Unmeasured refers to properties that are not metered which affects how much water is used by customers and creates some more uncertainty in this sub-component of overall water usage (when compared to measured). This provides a forecast of the water usage (consumption) of the properties that fall into this category. This figure applies to unmeasured non-household properties and excludes underground supply pipe leakage. This forecast represents the baseline position before any new investment or interventions. | 3.3572 | 3.3601 | 3.3629 | 3.3655 | 3.368 | 3.3727 | 3.3752 | 3.3775 | 3.3798 | 3.3821 | 3.3842 | 3.3864 | 3.3884 | 3.3904 | 3.3924 | 3.3943 | 3.3961 | 3.3979 | 3.3997 | 3.4014 | 3.403 | 3.4047 | 3.4062 | 3.4077 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092 | 3.4092
Measured (metered) household – consumption | Table 3: Baseline demand Row: 25BL | Ml/d | Households are those properties that are used as dwellings. Measured refers to properties that are metered which affects how much water is used by customers and provides a better forecast of overall water usage (when compared to unmeasured). This provides a forecast of the water usage (consumption) of the properties that fall into this category. This figure applies to billed measured and excludes underground supply pipe leakage. This forecast represents the baseline position before any new investment or interventions. | 88.3322 | 93.579 | 109.5533 | 136.3202 | 160.2949 | 176.2443 | 183.3379 | 185.6282 | 187.5962 | 189.6913 | 191.7782 | 193.8574 | 195.927 | 197.9982 | 200.0941 | 202.1697 | 204.263 | 206.3398 | 208.445 | 210.5566 | 212.648 | 214.9886 | 217.3185 | 219.6808 | 222.0424 | 223.6926 | 225.8764 | 228.0674 | 230.2628 | 232.4608 | 234.6623 | 236.8623 | 239.0594 | 241.2473 | 243.4247 | 245.5873 | 247.7262 | 249.8732 | 252.0347 | 254.2248 | 256.4569 | 258.632 | 260.8045 | 262.9752 | 265.1449 | 267.3143 | 269.485 | 271.6577 | 273.8334 | 276.0122 | 278.1936 | 280.3756 | 282.5543 | 284.7286 | 286.8991 | 289.0688 | 291.2449 | 293.4216 | 295.5988 | 297.7762
Unmeasured (unmetered) household – consumption | Table 3: Baseline demand Row: 26BL | Ml/d | Unmeasured refers to properties that are not metered which affects how much water is used by customers and creates some more uncertainty in this sub-component of overall water usage (when compared to measured). This provides a forecast of the water usage (consumption) of the properties that fall into this category. This figure applies to unmeasured household properties and excludes underground supply pipe leakage. This forecast represents the baseline position before any new investment or interventions. | 151.6498 | 146.9324 | 127.7352 | 93.2985 | 62.071 | 41.7907 | 33.308 | 31.4978 | 31.4016 | 31.1737 | 30.946 | 30.7418 | 30.5405 | 30.3389 | 30.1429 | 29.9466 | 29.7557 | 29.5642 | 29.3779 | 29.1939 | 29.0091 | 28.8549 | 28.6997 | 28.5489 | 28.3983 | 28.1349 | 27.9606 | 27.7869 | 27.6138 | 27.4406 | 27.2673 | 27.0932 | 26.9183 | 26.7417 | 26.5635 | 26.3834 | 26.2004 | 26.0187 | 25.8393 | 25.6643 | 25.4957 | 25.3175 | 25.139 | 24.9603 | 24.7815 | 24.6029 | 24.4246 | 24.2466 | 24.0691 | 23.892 | 23.7152 | 23.5384 | 23.3611 | 23.1831 | 23.0046 | 22.826 | 22.6485 | 22.471 | 22.2937 | 22.1162
Measured (metered) household – per capita consumption (PCC) | Table 3: Baseline demand Row: 29BL | l/h/d | Average amount of water used by each customer that lives in a measured (metered) household property in the zone. Measured in flow used (litres) per person (head) per day (l/h/d) This forecast represents the baseline position before any new investment or interventions. | 212.5 | 211 | 208.4 | 205.3 | 202.9 | 201.4 | 200.3 | 199.4 | 199.6 | 199.9 | 200.2 | 200.5 | 200.8 | 201.1 | 201.3 | 201.6 | 201.9 | 202.2 | 202.5 | 202.8 | 203 | 203.5 | 204 | 204.5 | 204.9 | 204.8 | 205.1 | 205.4 | 205.7 | 206 | 206.3 | 206.6 | 206.9 | 207.2 | 207.5 | 207.7 | 207.9 | 208.2 | 208.4 | 208.7 | 209 | 209.2 | 209.4 | 209.7 | 209.9 | 210.1 | 210.3 | 210.5 | 210.7 | 211 | 211.2 | 211.4 | 211.6 | 211.8 | 212 | 212.2 | 212.4 | 212.6 | 212.8 | 212.9
Unmeasured (unmetered) household – per capita consumption (PCC) | Table 3: Baseline demand Row: 30BL | l/h/d | Average amount of water used by each customer that lives in an unmeasured (unmetered) household property in the zone. Measured in flow used (litres) per person (head) per day (l/h/d) This forecast represents the baseline position before any new investment or interventions. | 271.5 | 271.6 | 272.2 | 273.3 | 275 | 277.9 | 280 | 280.9 | 281.7 | 281.3 | 280.9 | 280.8 | 280.6 | 280.4 | 280.3 | 280.1 | 280 | 279.9 | 279.8 | 279.7 | 279.6 | 279.8 | 280 | 280.2 | 280.4 | 279.7 | 279.7 | 279.7 | 279.7 | 279.8 | 279.8 | 279.8 | 279.8 | 279.9 | 279.8 | 279.8 | 279.7 | 279.7 | 279.6 | 279.7 | 279.7 | 279.7 | 279.7 | 279.7 | 279.7 | 279.6 | 279.6 | 279.6 | 279.6 | 279.6 | 279.6 | 279.6 | 279.6 | 279.5 | 279.5 | 279.5 | 279.5 | 279.5 | 279.5 | 279.4
Average household – per capita consumption (PCC) | Table 3: Baseline demand Row: 31BL | l/h/d | Average amount of water used by each customer that lives in a (metered or unmetered) household property in the zone. Measured in flow used (litres) per person (head) per day (l/h/d) This forecast represents the baseline position before any new investment or interventions. | 246.335 | 244.3042 | 238.4893 | 228.3538 | 218.9013 | 212.6157 | 209.4379 | 208.1847 | 208.3071 | 208.4454 | 208.5609 | 208.6702 | 208.8186 | 208.9168 | 209.0408 | 209.1604 | 209.3204 | 209.4654 | 209.6277 | 209.7895 | 209.9413 | 210.3109 | 210.6595 | 211.0279 | 211.3837 | 211.0983 | 211.3 | 211.5072 | 211.7141 | 211.9202 | 212.1263 | 212.3277 | 212.5235 | 212.7081 | 212.8807 | 213.0379 | 213.1723 | 213.3123 | 213.4634 | 213.6378 | 213.8467 | 214.0027 | 214.1546 | 214.3031 | 214.449 | 214.5931 | 214.7364 | 214.8797 | 215.0239 | 215.1688 | 215.314 | 215.4581 | 215.5976 | 215.732 | 215.8618 | 215.9894 | 216.1208 | 216.2512 | 216.3804 | 216.5082
Total leakage (total volume per day) | Table 3: Baseline demand Row: 40BL | Ml/d | Total losses through the underground distribution system (pipe network) and (customer’s) supply pipes. This should be consistent with the annual data return but should be based on the proportion that this zone contributes to the company’s total leakage. The total zonal leakage is expressed as a total volume lost per day (Ml/d) This forecast represents the baseline position before any new investment or interventions. | 44.4841 | 44.4773 | 44.4614 | 44.4489 | 44.4405 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118 | 44.2118
Total leakage (flow per property) | Table 3: Baseline demand Row: 41BL | l/prop/day | Total losses through the underground distribution system and (customer’s) supply pipes. This should be consistent with the annual data return but should be based on the proportion that this zone contributes to the company’s total leakage. The total zonal leakage is expressed as a volume (in litres) lost per property per day (l/prop/day). This forecast represents the baseline position before any new investment or interventions. | 117.6518 | 116.3364 | 115.0255 | 113.7511 | 112.5137 | 110.7504 | 109.5904 | 108.4539 | 107.3404 | 106.2492 | 105.1795 | 104.1308 | 103.1025 | 102.094 | 101.1047 | 100.1341 | 99.1817 | 98.2469 | 97.3294 | 96.4286 | 95.5441 | 94.6754 | 93.8222 | 92.984 | 92.1605 | 91.3427 | 90.5393 | 89.7499 | 88.9741 | 88.2117 | 87.4622 | 86.7253 | 86.0007 | 85.2882 | 84.5873 | 83.8979 | 83.2196 | 82.5522 | 81.8954 | 81.249 | 80.6127 | 79.9864 | 79.3696 | 78.7623 | 78.1642 | 77.5752 | 76.9949 | 76.4233 | 75.8601 | 75.3051 | 74.7582 | 74.2192 | 73.6879 | 73.1641 | 72.6478 | 72.1387 | 71.6366 | 71.1415 | 70.6532 | 70.1716
Measured (metered) properties (excl voids) | Table 3: Baseline demand Row: 45BL | 000s | This is the total number of metered properties that the company has on its database (household and non-household). Void properties (voids) are defined as the household properties, within the zone, which are connected for a water service but do not receive a bill, as there are no occupants. These are forecasted going forward based on growth projections. | 144.9851 | 155.7506 | 186.2245 | 237.1377 | 283.6144 | 315.3821 | 331.1309 | 337.9094 | 342.4477 | 346.9844 | 351.5197 | 356.0535 | 360.5858 | 365.1167 | 369.6461 | 374.1741 | 378.7006 | 383.2257 | 387.7494 | 392.2717 | 396.7926 | 401.3122 | 405.8303 | 410.3471 | 414.8625 | 419.4082 | 423.9327 | 428.453 | 432.9769 | 437.5007 | 442.0246 | 446.5484 | 451.0723 | 455.5961 | 460.12 | 464.6438 | 469.1677 | 473.6915 | 478.2154 | 482.7392 | 487.263 | 491.7869 | 496.3107 | 500.8346 | 505.3584 | 509.8823 | 514.4061 | 518.93 | 523.4538 | 527.9777 | 532.5015 | 537.0254 | 541.5492 | 546.073 | 550.5969 | 555.1207 | 559.6446 | 564.1684 | 568.6923 | 573.2161
Total properties – measured and unmeasured (incl. voids) | Table 3: Baseline demand Row: 48BL | 000s | All properties that the company has on its database (in the zone. This is a total of all the household and non-household properties (both metered and unmetered). This includes void properties. These are forecasted going forward based on growth projections. | 378.0994 | 382.3164 | 386.5353 | 390.7559 | 394.9783 | 399.2024 | 403.4281 | 407.6554 | 411.8842 | 416.1146 | 420.3464 | 424.5797 | 428.8144 | 433.0504 | 437.2877 | 441.5264 | 445.7662 | 450.0073 | 454.2496 | 458.493 | 462.7376 | 466.9832 | 471.2299 | 475.4777 | 479.7264 | 484.0215 | 488.3165 | 492.6115 | 496.9066 | 501.2016 | 505.4967 | 509.7917 | 514.0868 | 518.3818 | 522.6769 | 526.9719 | 531.267 | 535.562 | 539.8571 | 544.1521 | 548.4472 | 552.7422 | 557.0373 | 561.3323 | 565.6273 | 569.9224 | 574.2174 | 578.5125 | 582.8075 | 587.1026 | 591.3976 | 595.6927 | 599.9877 | 604.2828 | 608.5778 | 612.8729 | 617.1679 | 621.463 | 625.758 | 630.0531
Total population | Table 3: Baseline demand Row: 53BL | 000s | The total number of people living in the zone. The starting population is typically derived from census data or from the Office of National Statistics (ONS). Future forecasts of population are based on Government predictions using the ONS and local authority plans. | 988.0933 | 998.4616 | 1009.0621 | 1019.7692 | 1030.1903 | 1039.9882 | 1049.0462 | 1057.6972 | 1066.2277 | 1074.6601 | 1083.1732 | 1091.7958 | 1100.1953 | 1108.887 | 1117.561 | 1126.1486 | 1134.626 | 1143.0795 | 1151.5936 | 1160.1439 | 1168.6368 | 1177.247 | 1185.8927 | 1194.579 | 1203.3064 | 1211.4775 | 1219.8489 | 1228.2098 | 1236.5796 | 1244.9495 | 1253.3193 | 1261.6892 | 1270.059 | 1278.4289 | 1286.7987 | 1295.1686 | 1303.5384 | 1311.9083 | 1320.2782 | 1328.648 | 1337.0179 | 1345.3877 | 1353.7576 | 1362.1274 | 1370.4973 | 1378.8671 | 1387.237 | 1395.6068 | 1403.9767 | 1412.3466 | 1420.7164 | 1429.0863 | 1437.4561 | 1445.826 | 1454.1958 | 1462.5657 | 1470.9355 | 1479.3054 | 1487.6753 | 1496.0451
Measured (metered) household – Average occupancy rate (excl voids) | Table 3: Baseline demand Row: 54BL | h/prop | Occupancy rate (people living in each property) for metered (measured) households. Measured as people (head) per property (h/prop) | 2.8665 | 2.8477 | 2.8232 | 2.8006 | 2.7858 | 2.7747 | 2.7646 | 2.7546 | 2.7445 | 2.7343 | 2.7246 | 2.7154 | 2.7058 | 2.6971 | 2.6887 | 2.6802 | 2.6716 | 2.6632 | 2.6551 | 2.6473 | 2.6395 | 2.6322 | 2.6251 | 2.6182 | 2.6117 | 2.6045 | 2.5979 | 2.5915 | 2.5852 | 2.579 | 2.573 | 2.5671 | 2.5613 | 2.5556 | 2.5501 | 2.5446 | 2.5393 | 2.534 | 2.5289 | 2.5238 | 2.5188 | 2.514 | 2.5092 | 2.5045 | 2.4999 | 2.4954 | 2.4909 | 2.4866 | 2.4823 | 2.478 | 2.4739 | 2.4698 | 2.4658 | 2.4619 | 2.458 | 2.4542 | 2.4504 | 2.4467 | 2.4431 | 2.4395
Unmeasured (unmetered) household - Average occupancy rate | Table 3: Baseline demand Row: 55BL | h/prop | Occupancy rate (people living in each property) for unmetered (unmeasured) households. Measured as people (head) per property (h/prop) | 2.7416 | 2.742 | 2.7424 | 2.7427 | 2.7428 | 2.7429 | 2.7428 | 2.7428 | 2.7427 | 2.7426 | 2.7425 | 2.7424 | 2.7423 | 2.7422 | 2.7421 | 2.742 | 2.7419 | 2.7418 | 2.7417 | 2.7416 | 2.7415 | 2.7414 | 2.7413 | 2.7412 | 2.7411 | 2.741 | 2.7409 | 2.7407 | 2.7406 | 2.7405 | 2.7404 | 2.7403 | 2.7401 | 2.74 | 2.7399 | 2.7398 | 2.7396 | 2.7395 | 2.7394 | 2.7392 | 2.7391 | 2.739 | 2.7388 | 2.7387 | 2.7385 | 2.7384 | 2.7382 | 2.7381 | 2.7379 | 2.7378 | 2.7376 | 2.7375 | 2.7373 | 2.7371 | 2.737 | 2.7368 | 2.7366 | 2.7365 | 2.7363 | 2.7361
Total household metering penetration (incl. voids) | Table 3: Baseline demand Row: 57BL | % | The proportion of total household properties that receive bills based on metered consumption. The company will estimate the change year on year based on its current metering strategy and rates. This forecast represents the baseline position before any new investment or interventions. | 40.17% | 42.65% | 50.4% | 63.44% | 75.01% | 82.48% | 85.63% | 86.42% | 86.63% | 86.84% | 87.04% | 87.23% | 87.42% | 87.61% | 87.79% | 87.97% | 88.14% | 88.31% | 88.48% | 88.64% | 88.8% | 88.96% | 89.11% | 89.26% | 89.41% | 89.56% | 89.7% | 89.84% | 89.98% | 90.12% | 90.25% | 90.38% | 90.51% | 90.64% | 90.76% | 90.88% | 91% | 91.12% | 91.24% | 91.35% | 91.47% | 91.58% | 91.69% | 91.79% | 91.9% | 92% | 92.11% | 92.21% | 92.31% | 92.4% | 92.5% | 92.6% | 92.69% | 92.78% | 92.87% | 92.96% | 93.05% | 93.14% | 93.22% | 93.31%

## Table 4
Table 4 : Baseline supply demand balance
Company name |  |  | Affinity Water
WRZ name |  |  | Pinn
|  |  |  | Minimum Planning Period - 25 years | [24 empty] | Optional Planning Period
Data Requirement | WRMP19 reference | Units | Description | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54 | 2054-55 | 2055-56 | 2056-57 | 2057-58 | 2058-59 | 2059-60 | 2060-61 | 2061-62 | 2062-63 | 2063-64 | 2064-65 | 2065-66 | 2066-67 | 2067-68 | 2068-69 | 2069-70 | 2070-71 | 2071-72 | 2072-73 | 2073-74 | 2074-75 | 2075-76 | 2076-77 | 2077-78 | 2078-79 | 2079-80 | 2080-81 | 2081-82 | 2082-83 | 2083-84 | 2084-85 | 2085-86 | 2086-87 | 2087-88 | 2088-89 | 2089-90 | 2090-91 | 2091-92 | 2092-93 | 2093-94 | 2094-95 | 2095-96 | 2096-97 | 2097-98 | 2098-99 | 2099-100 | 2100-101
Distribution input (demand) | Table 4: Baseline supply demand balance Row: 11BL | Ml/d | The amount of water entering the distribution system (network) at the point of production e.g. water treatment works (to meet demands). This should be the average for the planning scenario. This is the baseline forecast which is the situation before any new investment or interventions. Calculated as a sum of water delivered (both household and non-household and measured and unmeasured), water taken unbilled, distribution system operational use, void properties and distribution losses. | 322.5396 | 323.2664 | 320.2328 | 312.7571 | 305.7037 | 301.3611 | 298.7024 | 299.205 | 301.1034 | 303.0002 | 304.8921 | 306.8039 | 308.714 | 310.6294 | 312.5792 | 314.5124 | 316.4727 | 318.4203 | 320.4059 | 322.4047 | 324.387 | 326.654 | 328.914 | 331.2158 | 333.5221 | 335.0075 | 337.0139 | 339.1097 | 341.2108 | 343.3141 | 345.4206 | 347.5237 | 349.6221 | 351.7084 | 353.781 | 355.8355 | 357.8624 | 359.8982 | 361.951 | 364.0385 | 366.1777 | 368.2559 | 370.3226 | 372.387 | 374.4504 | 376.5137 | 378.5788 | 380.6466 | 382.7183 | 384.7939 | 386.8725 | 388.9519 | 391.0273 | 393.0974 | 395.1625 | 397.2264 | 399.2977 | 401.3708 | 403.4444 | 405.518
Water Available For Use (WAFU) - own sources | Table 4: Baseline supply demand balance Row: 12BL | Ml/d | Baseline deployable output (supply) forecast less reductions in supplies (allowable outages, sustainability changes, raw water losses, and treatment works losses). Provides an estimate for average reliable supplies across the zone from the company’s own sources. This is the baseline position before any new investment or interventions. | 267.0914 | 267.107 | 267.0099 | 266.7794 | 266.5615 | 266.4254 | 266.3837 | 266.3981 | 266.4543 | 266.5103 | 266.5661 | 266.6223 | 266.6784 | 266.7345 | 266.7915 | 266.8478 | 266.9049 | 266.9615 | 267.019 | 267.0769 | 267.1341 | 267.1997 | 267.2649 | 267.3312 | 267.3976 | 267.4392 | 267.4995 | 267.56 | 267.6206 | 267.6814 | 267.7422 | 267.803 | 267.8637 | 267.924 | 267.984 | 268.0435 | 268.1021 | 268.1611 | 268.2206 | 268.281 | 268.3429 | 268.4028 | 268.4627 | 268.5224 | 268.5821 | 268.6419 | 268.7016 | 268.7615 | 268.8214 | 268.8815 | 268.9416 | 269.0018 | 269.0618 | 269.1217 | 269.1815 | 269.2412 | 269.3011 | 269.3611 | 269.4211 | 269.4811
Total Water Available For Use (WAFU) – including transfers | Table 4: Baseline supply demand balance Row: 13BL | Ml/d | Water Available For Use (including transfers) accounts for transfers (imports and exports) from third parties. This is essentially the final supply forecast having accounted for all supply components. This is the baseline position before any new investment or interventions. | 281.2914 | 281.307 | 281.2099 | 280.9794 | 280.7615 | 280.6254 | 280.5837 | 280.5981 | 280.6543 | 280.7103 | 280.7661 | 280.8223 | 280.8784 | 280.9345 | 280.9915 | 281.0478 | 281.1049 | 281.1615 | 281.219 | 281.2769 | 281.3341 | 281.3997 | 281.4649 | 281.5312 | 281.5976 | 281.6392 | 281.6995 | 281.76 | 281.8206 | 281.8814 | 281.9422 | 282.003 | 282.0637 | 282.124 | 282.184 | 282.2435 | 282.3021 | 282.3611 | 282.4206 | 282.481 | 282.5429 | 282.6028 | 282.6627 | 282.7224 | 282.7821 | 282.8419 | 282.9016 | 282.9615 | 283.0214 | 283.0815 | 283.1416 | 283.2018 | 283.2618 | 283.3217 | 283.3815 | 283.4412 | 283.5011 | 283.5611 | 283.6211 | 283.6811
Target Headroom (uncertainty) | Table 4: Baseline supply demand balance Row: 16BL | Ml/d | The uncertainty ‘headroom’ is required between the supply and demand forecasts to ensure the zone is balanced or in a surplus. If the difference between supply and demand is less than the target headroom then the zone is in deficit (i.e. actual headroom is less than target headroom). | 32.3719 | 32.0892 | 31.8066 | 31.524 | 31.2413 | 30.9587 | 30.676 | 30.3934 | 30.1107 | 29.8281 | 29.5454 | 29.2628 | 28.9802 | 28.6975 | 28.4149 | 28.1322 | 27.8496 | 27.5669 | 27.2843 | 27.0017 | 26.719 | 26.4364 | 26.1537 | 25.8711 | 25.5884 | 25.3058 | 25.0232 | 24.7405 | 24.4579 | 24.1752 | 23.8926 | 23.6099 | 23.3273 | 23.0447 | 22.762 | 22.4794 | 22.1967 | 21.9141 | 21.6314 | 21.3488 | 21.0661 | 20.7835 | 20.5009 | 20.2182 | 19.9356 | 19.6529 | 19.3703 | 19.0876 | 18.805 | 18.5224 | 18.2397 | 17.9571 | 17.6744 | 17.3918 | 17.1091 | 16.8265 | 16.5439 | 16.2612 | 15.9786 | 15.6959
Supply Demand Balance | Table 4: Baseline supply demand balance Row: 18BL | l/h/d | The difference between total water available for use (WAFU) and total demand forecast also accounting for target headroom. The supply demand balance calculation accounts for total water available for use (supply), target headroom (uncertainty) and distribution input (demand). This is the baseline position before any new investment or interventions. | -73.6201 | -74.0486 | -70.8295 | -63.3016 | -56.1835 | -51.6943 | -48.7947 | -49.0002 | -50.5599 | -52.118 | -53.6715 | -55.2444 | -56.8158 | -58.3925 | -60.0026 | -61.5968 | -63.2174 | -64.8258 | -66.4712 | -68.1295 | -69.7719 | -71.6907 | -73.6028 | -75.5557 | -77.513 | -78.6741 | -80.3376 | -82.0902 | -83.848 | -85.608 | -87.3709 | -89.1306 | -90.8858 | -92.629 | -94.359 | -96.0714 | -97.757 | -99.4512 | -101.1619 | -102.9063 | -104.7009 | -106.4366 | -108.1608 | -109.8828 | -111.6038 | -113.3248 | -115.0474 | -116.7728 | -118.5019 | -120.2348 | -121.9706 | -123.7072 | -125.4399 | -127.1675 | -128.8902 | -130.6117 | -132.3404 | -134.0709 | -135.8018 | -137.5329

## Table 5
Table 5 : Final plan supply forecast
Company name |  |  | Affinity Water
WRZ name |  |  | Pinn
|  |  |  | Minimum Planning Period - 25 years | [24 empty] | Optional Planning Period
Data Requirement | WRMP19 reference | Units | Description | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54 | 2054-55 | 2055-56 | 2056-57 | 2057-58 | 2058-59 | 2059-60 | 2060-61 | 2061-62 | 2062-63 | 2063-64 | 2064-65 | 2065-66 | 2066-67 | 2067-68 | 2068-69 | 2069-70 | 2070-71 | 2071-72 | 2072-73 | 2073-74 | 2074-75 | 2075-76 | 2076-77 | 2077-78 | 2078-79 | 2079-80 | 2080-81 | 2081-82 | 2082-83 | 2083-84 | 2084-85 | 2085-86 | 2086-87 | 2087-88 | 2088-89 | 2089-90 | 2090-91 | 2091-92 | 2092-93 | 2093-94 | 2094-95 | 2095-96 | 2096-97 | 2097-98 | 2098-99 | 2099-100 | 2100-101
Deployable output forecast (supply) | Table 7: Final planning water supply Row: 7FP | Ml/d | This gives a measure of water supply available (at treatment works outlet based on planned level of service and critical period) in the current situation. Deployable output is a building block in determining water supplies available for use and is defined as the output for specified conditions for a water resources system as constrained by; hydrological (source) yield; licensed quantities; abstraction assets; raw water transfer assets; treatment; water quality; and levels of service. This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 270.246 | 270.2617 | 270.1645 | 269.934 | 269.7161 | 274.58 | 274.5383 | 274.5527 | 274.6089 | 274.6649 | 274.7207 | 274.7769 | 274.833 | 277.8891 | 277.9461 | 278.0024 | 278.0595 | 287.8661 | 287.9236 | 287.9815 | 288.0387 | 288.1043 | 284.5683 | 287.3412 | 288.3022 | 288.3438 | 288.4041 | 288.4646 | 288.5253 | 288.586 | 288.6468 | 288.7076 | 288.7683 | 288.8286 | 279.1386 | 279.1981 | 279.2568 | 279.3157 | 279.3752 | 279.4356 | 281.8665 | 285.8091 | 289.3673 | 289.427 | 289.4868 | 290.5465 | 280.8562 | 280.9161 | 280.976 | 281.0361 | 281.0962 | 285.3268 | 290.5087 | 291.0263 | 291.0861 | 291.1458 | 291.2058 | 291.2657 | 291.3257 | 291.3857
Raw water losses, treatment works losses and operational use | Table 7: Final planning water supply Row: 9FP | Ml/d | The water losses as part of the raw water distribution and water treatment activities. Raw water distribution can include losses from pipes, mains, aqueducts, open channels, break pressure tanks and small reservoirs. Raw water operational use can include loss from regular washing-out of mains due to sediment build up and poor quality of source water. Treatment works losses are made up of structural water loss and both continuous and intermittent over-flows. Treatment works operational use includes water lost as a result of the treatment process, i.e. net loss that excludes water returned to source water. This may be calculated as the difference between total water abstracted and total distribution input (flow leaving treatment works to meet demand), or may consist of measured values of each component. This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364 | 0.84364
Outage allowance | Table 7: Final planning water supply Row: 10FP | Ml/d | Supplies via treatment works and abstraction assets are not always available. They will be temporarily unavailable due to both planned and unplanned maintenance. Generally outage only considers reductions in output for periods less than 3 months, outage for longer than 3 months in most cases will be reflected as a reduction in base deployable output. The outage allowance forecast is based on asset outages within the water resource zone that result in a reduction the amount of water available from treatment works. This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311 | 2.311

## Table 6
Table 6 : Final plan demand forecast
Company name |  |  | Affinity Water
WRZ name |  |  | Pinn
|  |  |  | Minimum Planning Period - 25 years | [24 empty] | Optional Planning Period
Data Requirement | WRMP19 reference | Units | Description | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54 | 2054-55 | 2055-56 | 2056-57 | 2057-58 | 2058-59 | 2059-60 | 2060-61 | 2061-62 | 2062-63 | 2063-64 | 2064-65 | 2065-66 | 2066-67 | 2067-68 | 2068-69 | 2069-70 | 2070-71 | 2071-72 | 2072-73 | 2073-74 | 2074-75 | 2075-76 | 2076-77 | 2077-78 | 2078-79 | 2079-80 | 2080-81 | 2081-82 | 2082-83 | 2083-84 | 2084-85 | 2085-86 | 2086-87 | 2087-88 | 2088-89 | 2089-90 | 2090-91 | 2091-92 | 2092-93 | 2093-94 | 2094-95 | 2095-96 | 2096-97 | 2097-98 | 2098-99 | 2099-100 | 2100-101
Measured (metered) non household – consumption | Table 8: Final planning water demand Row: 23FP | Ml/d | This provides a forecast of the water usage (consumption) of the properties that fall into metered non-household category. This figure applies to billed measured non-household properties and excludes underground supply pipe leakage. This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 32.0771 | 32.2784 | 32.4807 | 32.6848 | 32.8901 | 32.7831 | 31.1922 | 30.8935 | 30.5991 | 30.3077 | 30.3378 | 30.372 | 30.4114 | 30.4549 | 30.5024 | 30.8728 | 31.2474 | 31.6262 | 32.0095 | 32.3975 | 32.4715 | 32.5505 | 32.6343 | 32.723 | 32.8167 | 32.9153 | 32.9123 | 32.9907 | 33.0695 | 33.1481 | 33.2307 | 33.308 | 33.3842 | 33.4591 | 33.5325 | 33.6046 | 33.6756 | 33.7461 | 33.8169 | 33.8892 | 33.9649 | 34.0462 | 34.1189 | 34.1913 | 34.2637 | 34.3363 | 34.409 | 34.4821 | 34.5556 | 34.6294 | 34.7035 | 34.7777 | 34.8517 | 34.9254 | 34.9986 | 35.0714 | 35.1442 | 35.2179 | 35.2917 | 35.3654
Unmeasured (unmetered) non household – consumption | Table 8: Final planning water demand Row: 24FP | Ml/d | This provides a forecast of the water usage (consumption) of the properties that fall into the unmetered non-household category. This figure applies to unmeasured non-household properties and excludes underground supply pipe leakage. This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 3.3572 | 3.3601 | 3.3629 | 3.3655 | 3.368 | 3.2831 | 3.1909 | 3.0932 | 3.0873 | 3.0812 | 3.0748 | 3.0681 | 3.0611 | 3.0538 | 3.0462 | 3.0382 | 3.03 | 3.0214 | 3.0124 | 3.0031 | 2.9935 | 2.9835 | 2.9732 | 2.9624 | 2.9513 | 2.9384 | 2.9251 | 2.9114 | 2.8973 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829 | 2.8829
Measured (metered) household – consumption | Table 8: Final planning water demand Row: 25FP | Ml/d | This provides a forecast of the water usage (consumption) of the properties that fall into the metered household category. This figure applies to billed measured household properties and excludes underground supply pipe leakage. This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 87.6212 | 91.5427 | 105.9324 | 130.3916 | 152.5296 | 167.6582 | 174.2487 | 176.3602 | 178.3177 | 179.9396 | 181.523 | 183.0033 | 184.3702 | 185.6385 | 187.2028 | 188.6989 | 190.0865 | 191.5082 | 192.9204 | 194.2992 | 195.6612 | 197.5589 | 199.4464 | 201.3663 | 203.6541 | 205.2305 | 207.3404 | 209.5314 | 211.7269 | 213.9248 | 216.1264 | 218.3263 | 220.5234 | 222.7114 | 224.8887 | 227.0513 | 229.1902 | 231.3045 | 233.4332 | 235.5906 | 237.79 | 239.9323 | 242.1376 | 244.341 | 246.5434 | 248.7456 | 250.949 | 253.1217 | 255.2974 | 257.4763 | 259.6576 | 261.8396 | 264.0183 | 266.1927 | 268.3631 | 270.5328 | 272.7089 | 274.8857 | 277.0629 | 279.2402
Unmeasured (unmetered) household - consumption | Table 8: Final planning water demand Row: 26FP | Ml/d | This provides a forecast of the water usage (consumption) of the properties that fall into the unmetered household category. This figure applies to unmeasured household properties and excludes underground supply pipe leakage. This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 151.6498 | 146.9324 | 127.7352 | 93.2985 | 62.071 | 41.7907 | 33.308 | 31.4978 | 31.4016 | 31.1737 | 30.946 | 30.7418 | 30.5405 | 30.3389 | 30.1429 | 29.9466 | 29.7557 | 29.5642 | 29.3779 | 29.1939 | 29.0091 | 28.8549 | 28.6997 | 28.5489 | 28.3983 | 28.1349 | 27.9606 | 27.7869 | 27.6138 | 27.4406 | 27.2673 | 27.0932 | 26.9183 | 26.7417 | 26.5635 | 26.3834 | 26.2004 | 26.0187 | 25.8393 | 25.6643 | 25.4957 | 25.3175 | 25.139 | 24.9603 | 24.7815 | 24.6029 | 24.4246 | 24.2466 | 24.0691 | 23.892 | 23.7152 | 23.5384 | 23.3611 | 23.1831 | 23.0046 | 22.826 | 22.6485 | 22.471 | 22.2937 | 22.1162
Measured (metered) household – per capita consumption (PCC) | Table 8: Final planning water demand Row: 29FP | l/h/d | Average amount of water used by each customer that lives in a measured (metered) household property in the zone. Measured in flow used (litres) per person (head) per day (l/h/d). This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 211 | 206 | 201 | 196 | 193 | 192 | 190 | 189 | 190 | 190 | 190 | 189 | 189 | 189 | 188 | 188 | 188 | 188 | 187 | 187 | 187 | 187 | 187 | 187 | 188 | 188 | 188 | 189 | 189 | 190 | 190 | 190 | 191 | 191 | 192 | 192 | 192 | 193 | 193 | 193 | 194 | 194 | 194 | 195 | 195 | 196 | 196 | 196 | 196 | 197 | 197 | 197 | 198 | 198 | 198 | 199 | 199 | 199 | 199 | 200
Unmeasured (unmetered) household – per capita consumption (PCC) | Table 8: Final planning water demand Row: 30FP | l/h/d | Average amount of water used by each customer that lives in an unmeasured (unmetered) household property in the zone. Measured in flow used (litres) per person (head) per day (l/h/d) This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions) | 271 | 272 | 272 | 273 | 275 | 278 | 280 | 281 | 282 | 281 | 281 | 281 | 281 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 279 | 279 | 279 | 279 | 279
Average household – per capita consumption (PCC) | Table 8: Final planning water demand Row: 31FP | l/h/d | Average amount of water used by each customer that lives in a (metered or unmetered) household property in the zone. Measured in flow used (litres) per person (head) per day (l/h/d). This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 245.6052 | 242.2358 | 234.8501 | 222.4578 | 211.257 | 204.2431 | 200.651 | 199.2983 | 199.4815 | 199.242 | 198.9578 | 198.5859 | 198.1625 | 197.6083 | 197.3364 | 197.0219 | 196.6401 | 196.296 | 195.9436 | 195.5638 | 195.184 | 195.2781 | 195.3561 | 195.4582 | 195.8631 | 195.6221 | 195.8702 | 196.184 | 196.4963 | 196.8062 | 197.1148 | 197.4172 | 197.7128 | 197.9957 | 198.2654 | 198.5184 | 198.7474 | 198.9555 | 199.1737 | 199.4144 | 199.6888 | 199.9094 | 200.1742 | 200.4342 | 200.6902 | 200.9429 | 201.1936 | 201.4193 | 201.6448 | 201.8701 | 202.0946 | 202.3171 | 202.5341 | 202.7452 | 202.9506 | 203.1531 | 203.3585 | 203.562 | 203.7634 | 203.9627
Total leakage (total volume per day) | Table 8: Final planning water demand Row: 40FP | Ml/d | Total losses through the underground distribution system (pipe network) and (customer’s) supply pipes. This should be consistent with the annual data return but should be based on the proportion that this zone contributes to the company’s total leakage. The total zonal leakage is expressed as a total volume lost per day (Ml/d). This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 43.8872 | 41.034 | 37.0355 | 33.6648 | 30.9884 | 30.6107 | 30.5492 | 30.5813 | 30.6258 | 30.5929 | 30.5378 | 30.4755 | 30.4062 | 30.3304 | 30.2481 | 30.1825 | 30.0832 | 29.997 | 29.9026 | 29.798 | 28.9357 | 28.031 | 27.1265 | 25.7587 | 24.4855 | 24.4613 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371 | 24.4371
Total leakage (flow per property) | Table 8: Final planning water demand Row: 41FP | l/prop/day | Total losses through the underground distribution system and (customer’s) supply pipes. This should be consistent with the annual data return but should be based on the proportion that this zone contributes to the company’s total leakage. The total zonal leakage is expressed as a volume (in litres) lost per property per day (l/prop/day). This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 116.0733 | 107.33 | 95.8141 | 86.153 | 78.456 | 76.6795 | 75.724 | 75.0176 | 74.3554 | 73.5204 | 72.649 | 71.7779 | 70.9077 | 70.0389 | 69.1721 | 68.3595 | 67.4866 | 66.6588 | 65.8286 | 64.9912 | 62.5315 | 60.0258 | 57.5654 | 54.1744 | 51.0405 | 50.5376 | 50.0435 | 49.6072 | 49.1784 | 48.757 | 48.3427 | 47.9354 | 47.5349 | 47.1411 | 46.7537 | 46.3726 | 45.9977 | 45.6288 | 45.2658 | 44.9085 | 44.5568 | 44.2106 | 43.8697 | 43.5341 | 43.2035 | 42.8779 | 42.5572 | 42.2412 | 41.9299 | 41.6232 | 41.3209 | 41.023 | 40.7293 | 40.4398 | 40.1544 | 39.873 | 39.5955 | 39.3218 | 39.052 | 38.7857
Measured (metered) properties (excl voids) | Table 8: Final planning water demand Row: 45FP | 000s | This is the total number of metered properties that the company has on its database (household and non-household). Void properties (voids) are defined as the household properties, within the zone, which are connected for a water service but do not receive a bill, as there are no occupants. These are forecasted going forward based on growth projections. This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 144.9851 | 155.7506 | 186.2245 | 237.1377 | 283.6144 | 315.3821 | 331.1309 | 337.9094 | 342.4477 | 346.9844 | 351.5197 | 356.0535 | 360.5858 | 365.1167 | 369.6461 | 374.1741 | 378.7006 | 383.2257 | 387.7494 | 392.2717 | 396.7926 | 401.3122 | 405.8303 | 410.3471 | 414.8625 | 419.4082 | 423.9327 | 428.453 | 432.9769 | 437.5007 | 442.0246 | 446.5484 | 451.0723 | 455.5961 | 460.12 | 464.6438 | 469.1677 | 473.6915 | 478.2154 | 482.7392 | 487.263 | 491.7869 | 496.3107 | 500.8346 | 505.3584 | 509.8823 | 514.4061 | 518.93 | 523.4538 | 527.9777 | 532.5015 | 537.0254 | 541.5492 | 546.073 | 550.5969 | 555.1207 | 559.6446 | 564.1684 | 568.6923 | 573.2161
Total household metering penetration (incl. voids) | Table 8: Final planning water demand Row: 57FP | % | The forecast proportion of total household properties that receive bills based on metered consumption. The company will estimate the change year on year based on current metering strategy and rates. This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 40.17% | 42.65% | 50.4% | 63.44% | 75.01% | 82.48% | 85.63% | 86.42% | 86.63% | 86.84% | 87.04% | 87.23% | 87.42% | 87.61% | 87.79% | 87.97% | 88.14% | 88.31% | 88.48% | 88.64% | 88.8% | 88.96% | 89.11% | 89.26% | 89.41% | 89.56% | 89.7% | 89.84% | 89.98% | 90.12% | 90.25% | 90.38% | 90.51% | 90.64% | 90.76% | 90.88% | 91% | 91.12% | 91.24% | 91.35% | 91.47% | 91.58% | 91.69% | 91.79% | 91.9% | 92% | 92.11% | 92.21% | 92.31% | 92.4% | 92.5% | 92.6% | 92.69% | 92.78% | 92.87% | 92.96% | 93.05% | 93.14% | 93.22% | 93.31%

## Table 7
Table 7: Final plan supply demand balance
Company name |  |  | Affinity Water
WRZ name |  |  | Pinn
|  |  |  | Minimum Planning Period - 25 years | [24 empty] | Optional Planning Period
Data Requirement | WRMP19 reference | Units | Description | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54 | 2054-55 | 2055-56 | 2056-57 | 2057-58 | 2058-59 | 2059-60 | 2060-61 | 2061-62 | 2062-63 | 2063-64 | 2064-65 | 2065-66 | 2066-67 | 2067-68 | 2068-69 | 2069-70 | 2070-71 | 2071-72 | 2072-73 | 2073-74 | 2074-75 | 2075-76 | 2076-77 | 2077-78 | 2078-79 | 2079-80 | 2080-81 | 2081-82 | 2082-83 | 2083-84 | 2084-85 | 2085-86 | 2086-87 | 2087-88 | 2088-89 | 2089-90 | 2090-91 | 2091-92 | 2092-93 | 2093-94 | 2094-95 | 2095-96 | 2096-97 | 2097-98 | 2098-99 | 2099-100 | 2100-101
Distribution input (demand) | Table 9: Final planning supply demand balance Row: 11FP | Ml/d | The amount of water entering the distribution system (network) at the point of production e.g. water treatment works (to meet demands). This should be the average for the planning scenario. This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). Calculated as a sum of water delivered (both household and non-household and measured and unmeasured), water taken unbilled, distribution system operational use, void properties and distribution losses. | 321.2317 | 317.7868 | 309.186 | 296.0443 | 284.4863 | 278.7649 | 275.128 | 275.0651 | 276.6707 | 277.7343 | 279.0585 | 280.2999 | 281.4287 | 282.4557 | 283.7816 | 285.3783 | 286.8419 | 288.356 | 289.862 | 291.3309 | 291.7101 | 292.6181 | 293.5192 | 293.9986 | 294.9451 | 296.3195 | 298.2146 | 300.2967 | 302.3837 | 304.4727 | 306.5835 | 308.6866 | 310.7851 | 312.8713 | 314.9439 | 316.9985 | 319.0253 | 321.0284 | 323.0485 | 325.1032 | 327.2097 | 329.2552 | 331.3546 | 333.4517 | 335.5478 | 337.6439 | 339.7417 | 341.8095 | 343.8813 | 345.9568 | 348.0354 | 350.1148 | 352.1902 | 354.2603 | 356.3254 | 358.3893 | 360.4607 | 362.5337 | 364.6073 | 366.681
Water Available For Use (WAFU) - own sources | Table 9: Final planning supply demand balance Row: 12FP | Ml/d | Final plan deployable output (supply) forecast less reductions in supplies (allowable outages, sustainability changes, raw water losses, and treatment works losses). Provides the final planning estimate for average reliable supplies across the zone. This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 267.0914 | 267.107 | 267.0099 | 266.7794 | 266.5615 | 271.4254 | 271.3837 | 271.3981 | 271.4543 | 271.5103 | 271.5661 | 271.6223 | 271.6784 | 274.7345 | 274.7915 | 274.8478 | 274.9049 | 284.7115 | 284.769 | 284.8269 | 284.8841 | 284.9497 | 281.4137 | 284.1866 | 285.1476 | 285.1892 | 285.2495 | 285.31 | 285.3706 | 285.4314 | 285.4922 | 285.553 | 285.6137 | 285.674 | 275.984 | 276.0435 | 276.1021 | 276.1611 | 276.2206 | 276.281 | 278.7118 | 282.6545 | 286.2127 | 286.2724 | 286.3321 | 287.3919 | 277.7016 | 277.7615 | 277.8214 | 277.8815 | 277.9416 | 282.1722 | 287.3541 | 287.8717 | 287.9315 | 287.9912 | 288.0511 | 288.1111 | 288.1711 | 288.2311
Total Water Available For Use (WAFU) – including transfers | Table 9: Final planning supply demand balance Row: 13FP | Ml/d | Water Available For Use (including transfers) accounts for transfers (imports and exports) from third parties. This is essentially the final supply forecast having accounted for all supply components. This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 358.3998 | 356.2956 | 348.6241 | 338.1987 | 322.8457 | 325.5391 | 322.2211 | 322.8369 | 324.1004 | 329.4601 | 328.1164 | 329.5678 | 330.6516 | 334.6999 | 333.0162 | 333.9821 | 335.2078 | 336.6086 | 388.4322 | 390.1213 | 391.472 | 390.6239 | 342.4248 | 344.2673 | 346.4822 | 348.0165 | 349.9461 | 351.7205 | 353.5002 | 355.2822 | 357.0672 | 358.849 | 360.626 | 362.3909 | 364.1421 | 365.8753 | 367.5807 | 369.2995 | 371.031 | 372.7971 | 374.6149 | 376.3717 | 378.117 | 379.86 | 381.602 | 383.344 | 385.0876 | 386.8341 | 388.5844 | 390.3386 | 392.0958 | 393.8538 | 395.6078 | 397.3565 | 399.1003 | 400.8428 | 402.5927 | 404.3444 | 406.0966 | 407.8489
Target Headroom (uncertainty) | Table 9: Final planning supply demand balance Row: 16FP | Ml/d | The uncertainty ‘headroom’ is required between the supply and demand forecasts to ensure the zone is balanced or in a surplus. If the difference between supply and demand is less than the target headroom then the zone is in deficit (i.e. actual headroom is less than target headroom). | 32.3719 | 32.0892 | 31.8066 | 31.524 | 31.2413 | 31.4849 | 31.1635 | 30.8421 | 30.5207 | 30.1993 | 29.8779 | 29.5565 | 29.2351 | 28.9138 | 28.5924 | 28.271 | 27.9496 | 27.6282 | 27.3068 | 26.9854 | 26.664 | 26.3427 | 26.0213 | 25.6999 | 25.3785 | 25.0571 | 24.7357 | 24.4143 | 24.093 | 23.7716 | 23.4502 | 23.1288 | 22.8074 | 22.486 | 22.1646 | 21.8432 | 21.5219 | 21.2005 | 20.8791 | 20.5577 | 20.2363 | 19.9149 | 19.5935 | 19.2721 | 18.9508 | 18.6294 | 18.308 | 17.9866 | 17.6652 | 17.3438 | 17.0224 | 16.7011 | 16.3797 | 16.0583 | 15.7369 | 15.4155 | 15.0941 | 14.7727 | 14.4513 | 14.13
Supply Demand Balance | Table 9: Final planning supply demand balance Row: 18FP | Ml/d | The difference between total water available for use (WAFU) and total demand forecast also accounting for target headroom. The supply demand balance calculation accounts for total water available for use (supply), target headroom (uncertainty) and distribution input (demand). This forecast is for the final plan and assumes delivery of the preferred options (new investments and interventions). | 4.7962 | 6.4196 | 7.6316 | 10.6304 | 7.118 | 15.2893 | 15.9297 | 16.9297 | 16.909 | 21.5265 | 19.18 | 19.7114 | 19.9877 | 23.3305 | 20.6422 | 20.3329 | 20.4163 | 20.6244 | 71.2633 | 71.805 | 73.0978 | 71.6632 | 22.8844 | 24.5688 | 26.1586 | 26.6399 | 26.9958 | 27.0094 | 27.0235 | 27.0379 | 27.0335 | 27.0335 | 27.0335 | 27.0335 | 27.0335 | 27.0335 | 27.0335 | 27.0707 | 27.1034 | 27.1361 | 27.1689 | 27.2016 | 27.1689 | 27.1361 | 27.1034 | 27.0707 | 27.0379 | 27.0379 | 27.0379 | 27.0379 | 27.0379 | 27.0379 | 27.0379 | 27.0379 | 27.0379 | 27.0379 | 27.0379 | 27.0379 | 27.0379 | 27.0379

## Table 8
Table 8: Final plan option costs
Company name |  |  | Affinity Water
WRZ name |  |  | Pinn
Data Requirement | WRMP19 reference | Units | Description | Scheme 1 | Scheme 2 | Scheme 3 | Scheme 4 | Scheme 5 | Scheme 6 | Scheme 7 | Scheme 8 | Scheme 9 | Scheme 10 | Scheme 11 | Scheme 12 | Scheme 13 | Scheme 14 | Scheme 15 | Scheme 16 | Scheme 17 | Scheme 18 | Scheme 19 | Scheme 20 | Scheme 21 | Scheme 22 | Scheme 23 | Scheme 24 | Scheme 25 | Scheme 26 | Scheme 27 | Scheme 28 | Scheme 29 | Scheme 30 | Scheme 31 | Scheme 32 | Scheme 33 | Scheme 34 | Scheme 35
Option name | Table 5: Feasible options Column C | Text | Name of scheme for referencing. | AFF-TPO-WRZ4-0412 | AFF-RES-WRZ4-0832 | AFF-NGW-WRZ4-0624 | AFF-RTR-WRZ4-4018 | AFF-RTR-WRZ4-4017 | AFF-RTR-WRZ4-4012 | AFF-RTR-WRZ4-4011 | AFF-NTW-WRZ4-1005 | AFF-NTW-WRZ4-1003 | Iver LGS Development | AFF-CTR-WRZ4-4025 | AFF-RTR-WRZ4-4023 | AFF-CTR-WRZ4-4004 | AFF-CTR-WRZ4-4002 | AFF-CTR-WRZ4-4001 | AFF-CTR-WRZ4-0750 | AFF-CTR-WRZ4-0707 | AFF-LEA-WRZ4-1012 | AFF-LEA-WRZ4-1009 | AFF-LEA-WRZ4-0423 | AFF-WEF-WRZ4-1000 | AFF-MET-WRZ4-0531 | AFF-MET-WRZ4-1010 | AFF-MET-WRZ4-0904 | AFF-WEF-WRZ4-1050 | AFF-REU-WRZ4-603 | AFF-WEF-WRZ4-0569 | AFF-WEF-WRZ4-0901 | AFF-WEF-WRZ4-0567
Option reference number | Table 5: Feasible options Column D | Text | Reference number used in WRMP tables | 412 | 832 | 624 | 4018 | 4017 | 4012 | 4011 | 1005 | 1003 |  | 4026 | 4023 | 4004 | 4002 | 4001 | 750 | 707 | 1012 | 1009 | 423 | 1000 | 531 | 1010 | 904 | 1050 | 603 | 569 | 901 | 567
Type of option | Table 5: Feasible options Column E | Text | Type of benefit the scheme delivers, e.g. Options to reduce outage, Options to increase raw imports, etc. | TPO | RES | NGW | RTR | RTR | RTR | RTR | NTW | NTW | NGW | CTR | RTR | CTR | CTR | CTR | CTR | CTR | LEA | LEA | LEA | WEF | MET | MET | MET | WEF | REU | WEF | WEF | WEF
Preferred option | Table 5: Feasible options Column F | Y/N | Defines whether the option that was considered was chosen for the companies’ short list of feasible options, or whether it is part of the preferred (final) plan and will form part of the companies water resources programme. | bar: TPO to WEF
Planned scheme start date | Table 5: Feasible options Column G | Year | First year that the scheme delivers full benefit (additional resource or demand saving) if in the preferred plan. This will be the planned delivery of the scheme as part of the company’s delivery programme and should be updated accordingly. | 2024 | 2028 | 2026 | 2035 | 2035 | 2035 | 2035 | 2028 | 2028 | 2033 | 2029 | 2021 | 2024 | 2023 | 2022 | 2027 | 2027 | 2030 | 2030 | 2020 | 2020 | 2020 | 2020 | 2029 | 2020 | 2020 | 2020 | 2020 | 2023
Option benefit – additional resources or demand saved (based on full implementation) | Table 5: Feasible options Column I | Ml/d on full implementation | Zonal benefit (in terms of additional supply – water available for use, or demand savings) of the option at full implementation. | 1 | 9.75 | 5 | 100 | 50 | 100 | 50 | 0 | 0 | 3 | 4 | 15 | 40 | 0 | 17 | 0 | 0 | 0.95293 | 3.7242 | 0.59261 | 1.5964 | 0.52634 | 3.7267 | 6.8255 | 7.807 | 0.16685 | 0.16365 | 0.65056 | 0.18812
Total planning period option benefit (Net Present Value) | Table 5: Feasible options Column J | Ml | The total volume (mega litres) of benefit gained from the option over the whole planning period. The benefit volume is then discounted over the planning period using the discount rate to provide a Net Present Value (NPV) of the benefit. | 9025.8589 | 76212.3167 | 43538.9125 | 606246.6515 | 303123.3257 | 606246.6515 | 303123.3257 | 0 | 0 | 27077.5768 | 41653.8257 | 150726.8462 | 361034.3567 | 0 | 164828.59 | 0 | 0 | 9402.7992 | 29213.0821 | 6171.1554 | 4696.345 | 4381.4329 | 9897.7348 | 55304.4814 | 64652.0074 | 1617.7247 | 260.8857 | 1539.656 | 320.8799
Total planning period capital cost of option (CAPEX NPV) | Table 5: Feasible options Column K | £000s | The total capital cost (CAPEX) spent to deliver the option over the planning period. This is then discounted over the planning period using the discount rate to provide a NPV of the total cost. | 6327.1983 | 43407.5923 | 13996.9257 | 419831.2621 | 214549.6498 | 477799.5095 | 243646.3419 | 95540.4705 | 54899.2376 | 9184.1124 | 0 | 3776.361 | 17910.3407 | 4992.357 | 1502.0305 | 38089.0518 | 62748.2852 | 6176.2929 | 44652.5045 | 160.15 | 0 | 57.8781 | 20 | 29089.5727 | 0 | 3632.8672 | 0 | 0 | 0
Total planning period operating cost of option (OPEX NPV) | Table 5: Feasible options Column L | £000s | The total operating cost (OPEX) spent to deliver the option over the planning period. This is then discounted over the planning period using the discount rate to provide a NPV of the total cost. | 3287.9281 | 23928.527 | 5191.8214 | 324958.8745 | 163094.7548 | 39504.5554 | 20358.9816 | 9560.6492 | 6682.1264 | 3432.5427 | 0 | 131365.7527 | 10703.1972 | 1991.9734 | 4897.2461 | 2860.0069 | 3104.4106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total planning period operating saving cost of option (OPEX saving NPV) | Table 5: Feasible options Column M | £000s | The total operating cost saving made through the delivery / operation of the option over the planning period. This is then discounted over the planning period using the discount rate to provide a NPV of the total cost. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total planning period carbon costs (Carbon NPV) | Table 5: Feasible options Column N | £000s | The total carbon cost (carbon generated through building and operating the option translated into financial terms) spent to deliver the option over the planning period. Two carbon prices have been developed: a traded price of carbon for emissions covered by the EU Emissions Trading Scheme (includes grid electricity use); and a non-traded price of carbon for emissions outside of the EU ETS. Companies use the appropriate carbon price depending on the origin of the fixed emissions (e.g. construction) and variable emissions (e.g. operational use). This is then discounted over the planning period using the discount rate to provide a NPV of the total carbon cost. | 1.0057 | 9.4576 | 6.3748 | 15631.0354 | 14836.4358 | 2091.5183 | 1296.9197 | 88.6856 | 40.938 | 5.6288 | 0 | 0 | 9.8061 | 0.523 | 0.01 | 22.5347 | 25.1777 | 531.6647 | 101.7804 | 0.11495 | 0.056555 | 0.007203 | 0 | 54.65 | 42.2153 | 20.7674 | 0.29255 | 1.8897 | 0.67733
Total planning period social and environmental costs (NPV) | Table 5: Feasible options Column O | £000s | The total social and environmental costs (both positive and negative) translated into financial terms to deliver and operate the option over the planning period. | 25.444 | 13129.0164 | 19938.6167 | 3444.116 | 3444.116 | 3444.116 | 3444.116 | 93.446 | 93.446 | 0 | 0 | 0 | 99.233 | 0.075 | 0 | 221.7138 | 366.1918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total planning period option cost (NPV) | Table 5: Feasible options Column P | £000s | The total overall cost for the delivery and operation of the option over the planning period. This is then discounted using the discount rate to provide a NPV of the total cost. | 9641.5761 | 80474.5933 | 39133.7386 | 763865.2879 | 395924.9564 | 522839.6992 | 268746.3593 | 105283.2512 | 61715.748 | 12622.2839 | 0 | 135142.1136 | 28722.577 | 6984.9284 | 6399.2866 | 41193.3072 | 66244.0653 | 6707.9575 | 44754.2849 | 160.265 | 0.056555 | 57.8853 | 20 | 29144.2227 | 42.2153 | 3653.6346 | 0.29255 | 1.8897 | 0.67733
Average Incremental Cost (AIC) | Table 5: Feasible options Column Q | p/m³ | Average incremental cost of option delivery and operation over the planning period. The extra cost (pence) per volume of water gained (m³) for the option. | 106.5287 | 88.3533 | 44.0726 | 122.8527 | 124.5844 | 85.329 | 87.095 |  |  | 46.5945 | 0 | 89.6603 | 7.9254 |  | 3.8824 |  |  | 65.6857 | 152.8511 | 2.5951 | 0 | 1.321 | 0.20207 | 52.5989 | 0 | 224.5665 | 0 | 0 | 0
Average Incremental Social & Environmental Cost (AISC) | Table 5: Feasible options Column R | p/m³ | Average incremental cost (including environmental and social costs) of option delivery and operation over the planning period. The extra cost (pence) per volume gained (m³) for the option. | 106.8217 | 105.5926 | 89.8822 | 125.9991 | 130.6151 | 86.2421 | 88.6591 |  |  | 46.6153 | 0 | 89.6603 | 7.9556 |  | 3.8824 |  |  | 71.34 | 153.1995 | 2.597 | 0.0012042 | 1.3212 | 0.20207 | 52.6978 | 0.065296 | 225.8502 | 0.11214 | 0.12273 | 0.21109
Scope Confidence | Table 5: Feasible options Column S | Score 1 to 5 | Measure of the confidence the company has in the scope (scheme type / benefits). For the purposes of long-term planning, companies initially develop schemes in outline and assign costs on that basis. As a result there is some uncertainty associated with that information. A score of 1 is an indication of low confidence whilst a 5 indicates relative high confidence.
Cost Confidence | Table 5: Feasible options Column T | Score 1 to 5 | Measure of the confidence the company has in the costs. For the purposes of long-term planning, companies initially develop schemes in outline and assign costs on that basis. As a result there is some uncertainty associated with that information. As a company develops its plans to the feasible options stage, there is an expectation that the robustness of estimates of costs improve so that there is sufficient confidence in the company‘s ability to implement its preferred solution as described. A score of 1 is an indication of low confidence whilst a 5 indicates relative high confidence.